## BFV
| AWWA BFV V501 |  | Where info came from |  | BF BFV | HP BFV | Plug | Swing Check | Ball | Flex Check | TDCV | Specialty Check | Gate | Knife Gate
AIS exempt / AIS Domestic/BABA/Buy American
Submittal Section | 40 05 60 |  | 40.05.64.1.03
O&M Section
Warranty Section | 01 78 36 |  | 40.05.64.4.06.A
Warranty Duration | 2 years |  | 01.78.36.1.05.F | NOTE - This would typically indicate a start date for the warranty - most commonly would be from shipment, substantial completion, or acceptance
AWWA | C504/C516/C519 |  | 40.05.64.1.01.A & 40.27.02.06.E.1.a
Reference Section | 40_05_60, 01 60 _00 |  | 40.05.64.1.01.B
Spec Section | 40 05 64 |  | 40.05.64 Page 1 Headline
Named Mfg | D, M, P, MH/K, GA, V |  | 40.5.64.2.02.A.2.A-E
Size | 3" - 24" | 30" - 72" | 40.05.64.2.01.1 & 1.a
Ends | #125 FL | #125 FL | 40.05.64.2.02.2.02.A.1
Bi-Directional Test | Yes |  | 40.27.02.2.01.E
Pressure | 250B, Size actuators for full pressure |  | 40.05.64.1.01.A
Body | CI | DI | 40.05.64.2.01.1 & 1.a
Disc/Plug/Rotor | CI/DI | DI | 40.05.64.2.01.1 & 1.a
Shaft | 304 | 17-4 | 40.05.64.2.01.1 & 1.a
Seat | Bonded to body or disc, Neo, EPDM, Buna | MRS, Neo, EPDM, Buna | 40.05.64.2.01.1 & 1.a, 40.05.64.2.02A.4 & 5, 40.27.02.2.06.E.1.a.2
Mating Seat | 304 | 304 | 40.05.64.2.01.1 & 1.a
Bearings
Paint | 09 90 00 |  |  | There is a ton of info in this section that is needed, we only need info for shop painting. Field painting is for others. We'll be looking for mils thickness, paint type, paint mfg, holiday testing
NSF | NSF/61 |  | 40.27.02.2.06.E.1.a.10
Hardware
BSF/LL/Anti Cav |  |  |  | Backspot facing, Lifting Lugs, Anti Cavitation
Tags | SS 316 |  | 40.05.60.2.02.C
Actuator Sizing | Full range of pressures & velocities |  | 40.27.02.2.01.F
Manual Actuator | WG |  | 40.05.64.2.03.A.2 |  | 6" & up - LL
Manual Input Torque | 300 ft/lbs; 450 ft/lbs for buried |  | 40.5.64.2.03.A.3 & 40.27.2.06.E.1.a.8
Manual Actuator Enclosure | Buried = sub 20 |  | 40.27.02.2.07.A.3.b
Manual Actuator Vendors Named | Auma GS/Limitorque HBC |  | 40.05.64.2.03.B
Rim Pull | 40# |  | 40.05.60.2.01.C.3
CW | DI w/ SS Chain |  | 40.05.60.2.01.C.11
EMO Actuator | O/C or MOD |  | 40.27.02.C.3 & 4
EMO Actuator Vendors Named | 120V Rotork, =; 480V Rotork IQ, Limitorque L120, Auma SA/SAR |  | 40.27.02.2.07.B.7 & 40.27.02.C.7.a-c
EMO Actuator Enclosure | NEMA 250 Type 4 |  | 40.27.02.2.07.C.2.h
Pneumatic Actuator | Vane DA or SR |  | 40.27.02.2.07.D.2 .2f. & .2.g
Pneumatic Vendors Named | K-Tork, Kinetrol |  | 40.27.02.2.07.D.2.k
Pneumatic Enclosure |  |  | 40.27.02.2.07.D.22.
EH Actuator
EH Actuator Vendors Named | Rexa, Rotork Skilmatic SI |  | 40.2.07.E.3.6
EH Actuator Enclosure
Start Up | Min 1 Day/1 trip install & test, Min 2 days for performance test & cert of Installation each valve type over 30" |  | 40.05.64.3.02.A
OL/OR | OL |  | 40.05.60.2.01.A.4 & 40.27.02.G |  | OL | OL | OL | OL | OL | OL | OL | OL | OL | OL | OL
HW/CW/Nut
Ext Stem/Bonnet/FS
Submittal Requires | Spec Checks for Submittal |  | 40.5.64.1.03.B.1
Submittal Requires | Certificate of unit responsibility |  | 40.5.64.1.03.B.2
Submittal Requires | Test Procedures |  | 40.5.64.1.03.B.3.a
Submittal Requires | Proof of Design |  | 40.5.64.1.03.B.3.b
| Turns to open |  | 40.5.64.1.03.B.3.c
Submittal Requires | Weights |  | 40.5.64.1.03.B.3.d
Submittal Requires | Torque Runs |  | 40.5.64.1.03.B.3.e
Submittal Requires | COC |  | 40.5.64.1.03.B.3.f
Submittal Requires | O&M Data |  | 40.05.60.1.04.B.2
Submittal Requires | Sizing Calcs |  | 40.27.02.1.02.A.f
Witness Testing
QA | UT Required per 40 05 64.1.04.A.1-7 |  | 40.05.64.1.04.A.1-7
Spares required | 01.60.00.3.2.05
Adders:
O2 Cleaning for Air/Oxygen/Ozone or Chlorine
| Accessories |  | 40.27.02.2.08
Exceptions/Clarifications: